## Slide 1
ABS-120GGB-M10
485W – 505W
Topcon Half Cut PV Module
Glass/Glass-Black Frame
KEY FEATURES
BETTER TEMPERTURE COEFFICIENT
Lower temperature coefficient (Pmax):
-0.30%/°C, increases energy yield in hot climate
LOW SYSTEM COST
Higher yield per surface area, lower BOS costs, higher power classes, and an efficiency rate of up to 23.34%.
ADVANCED MODULE TECHNOLOGY
Highest reliability & enhanced crack tolerance MBB module
PID
ENDURING HIGH PERFORMANCE
Anti LID and Anti PID Technology. Under long-term production safety conditions, the limited power degradation caused by the PID effect is guaranteed.
EXTREME WEATHER RATING
High-tech aluminum alloy frame, certified for high snow (5400 Pa) and wind loads (2400 Pa).
ALL-WEATHER TECHNOLOGY Optimal
Yields, whatever the weather, with low-light and temperature behaviour.
Residential
Utility
Off-Grid
Commercial
THE IDEAL SOLUTION FOR
COMPREHENSIVE CERTIFICATES
IEC 61215 | IEC 61730 | IEC 61701 | IEC 62716
LINEAR PERFORMANCE WARRANTY
12-year Warranty for Materials and Processing (1st year ≤ 1.0%, 2nd~30th years ≤ 0.40% / year)
30-year Warranty for Extra Linear Power Output
Product warranty
12
Years
Product warranty
30
Years
80%
85%
100%
99%
95%
1
5
10
15
25
30
90%
ADDED VALUE FROM WARRANTY
years
87.40%
20
Guaranteed Power Performance
MADE IN UAE
Premium products are 100% made in the Emirates.
A RELIABLE INVESTMENT
Products up to 725Wp, 30 years of performance warranty.
ENCOURAGING INNOVATION
Innovative, prestigious, European production technology
ADVANTAGES
MAXIMUM EFFICIENCY
23.3%
OUTPUT POSITIVE TOLERANCE
Guaranteed 0~+10W positive tolerance ensures power output reliability.
MAXIMUM POWER OUTPUT
+10W
505W
Address: Abundance Solar Panels Industries – LLC Plot No 7-8, KHIA5, KEZAD, Abu Dhabi, UAE
UL 61730 | CEC | ISO 9001 | ISO 14001| ISO 45001

## Slide 2
ENGINEERING DRAWINGS & TECHNICAL PARAMETERS
ABS-120GGB-M10-485-505W
ELECTRICAL CHARACTERISTICS (STC/NOCT)
Models | Maximum Rating Power (Pmax) (W) |  | Open Circuit Voltage (Voc) (V) |  | Maximum Power Voltage (Vmp) (V) |  | Short Circuit Current (Isc) (A) |  | Maximum Power Current (Imp) (A) |  | Module Eﬃciency (EFF)(%)
 | STC | NOCT | STC | NOCT | STC | NOCT | STC | NOCT | STC | NOCT | 
ABS-120GGB-M10-485 | 485 | 362.5 | 42.97 | 40.40 | 37.04 | 34.56 | 14.03 | 11.32 | 13.18 | 10.55 | 22.42%
ABS-120GGB-M10-490 | 490 | 366.3 | 43.11 | 40.53 | 37.16 | 34.67 | 14.08 | 11.36 | 13.29 | 10.64 | 22.65%
ABS-120GGB-M10-495 | 495 | 370.0 | 43.22 | 40.64 | 37.25 | 34.75 | 14.11 | 11.39 | 13.37 | 10.71 | 22.88%
ABS-120GGB-M10-500 | 500 | 373.7 | 43.31 | 40.72 | 37.33 | 34.83 | 14.13 | 11.40 | 13.45 | 10.77 | 23.11%
ABS-120GGB-M10-505 | 505 | 377.5 | 43.42 | 40.82 | 37.43 | 34.92 | 14.14 | 11.41 | 13.52 | 10.83 | 23.34%
BI-FACIAL OUTPUT-BACKSIDE POWER GAIN
Models |  | ABS-120GGB-M10-485 | ABS-120GGB-M10-490 | ABS-120GGB-M10-495 | ABS-120GGB-M10-500 | ABS-120GGB-M10-505
10% | Power | 534 | 539 | 545 | 550 | 556
 | Eff | 24.66% | 24.91% | 25.17% | 25.42% | 25.67%
15% | Power | 558 | 564 | 569 | 575 | 581
 | Eff | 25.78% | 26.04% | 26.31% | 26.58% | 26.84%
20% | Power | 582 | 588 | 594 | 600 | 606
 | Eff | 26.90% | 27.18% | 27.45% | 27.73% | 28.01%
25% | Power | 606 | 613 | 619 | 625 | 631
 | Eff | 28.02% | 28.31% | 28.60% | 28.89% | 29.17%
*Standard Test Condition (STC): Cell Temperature 25 °C, Irradiance 1000 W/m², AM 1.5, Nominal module operating temperature (NMOT): Air mass AM 1.5, Irradiance 800W/m², temperature 20°C, windspeed 1 m/s. Reduction in eﬃciency from 1000W/m² to 200W/m² at 25°C: 3.5 ± 2%. *Values without tolerance are typical numbers. Measurement tolerance: ± 3%```
Solar Cell | Topcon 182.2 x 91.88 mm M10 ,16BB
No.of cells | 120 (6×20)
Dimensions | 1908 mm x 1134 mm x 30 mm ( 75.11” x 44.65“ x 1.18” inch)
Weight | 26 kg / 57.32 lbs.(±3%)
Front Glass | 2.0 mm, High Transmission, Low Iron, Tempered ARC Glass
Cell Encapsulation | EPE(Expanded polyethylene) & EVA (Ethylene-Vinyl-Acetate)
Back Glass | 2.0 mm Semi Tempered Glass with Glaze
Frame | Black Anodized Aluminum Alloy Type 6005T6 , Black Color
Junction Box | IP68, 1500VDC, 3 Bypass Diodes
Connectors Type | IP68 MC4 Compatible
Cable | 400mm or 1300 mm, 4mm2
Package Conﬁguration | 36 pcs Per Pallet, 864 pcs per 40’ FT container ( Two pallets=One stack )
CURRENT-VOLTAGE CURVE UNDER DIFFERENT IRRADIANCE
1134±1
1908±1
FRONT VIEW
30
33
A-A
Laminate
Silicon Sealant
Frame
30
Laminate
Frame
15
B-B
Silicon Sealant
The Graphs are for reference purpose only. Please consult Abundance technical team for further clarifications.
Mechanical Load | 5400 Pa
Maximum System Voltage | 1500VDC
Series Fuse Rating | 25 A
Operating Temperature | -40 to 85 °C
Safety application class | Class II
Fire Rating | Class C
Nominal Module Operating Temperature | 43°C ± 2°C
Temperature Coeﬃcient of Isc | +0.05 % / °C
Temperature Coeﬃcient of Voc | -0.25 % / °C
Temperature Coeﬃcient of Pmax | -0.30 % / °C
OPERATING CONDITION
TEMPERATURE CHARACTERISTICS
MECHANICAL DATA
IV-CURVES
DIMENSIONS OF PV MODULE (mm)
Address: Abundance Solar Panels Industries – LLC Plot No 7-8, KHIA5, KEZAD, Abu Dhabi, UAE
BACK VIEW
B
C
1086± 2
400±1
1200±1
1400±1
A A
B B
800 W/ m 2
600 W/ m 2
400 W/ m 2
200 W/ m 2
25℃ 1000 W/ m 2
00
4
6
8
10
12
10
20
30
40
45
Voltage(V)
Current(A)
CURRENT-VOLTAGE CURVE UNDER DIFFERENT WORKING TEMPERATURES
14
1000 W/m 2
4
6
8
10
12
10℃
25℃
40℃
55℃
70℃
0
0 10
20
30
40
45
Voltage(V)
Current(A)
14
C-Mounting Hole 4 No’s
B-Mounting Hole 8 No’s