## Slide 1
ABS-132GWS-G12
705W – 725W
Topcon Half Cut PV Module
Glass/White Back Sheet -Silver Frame
KEY FEATURES
BETTER TEMPERTURE COEFFICIENT
Lower temperature coefficient (Pmax):
-0.30%/°C, increases energy yield in hot climate
LOW SYSTEM COST
Higher yield per surface area, lower BOS costs, higher power classes, and an efficiency rate of up to 23.34%.
ADVANCED MODULE TECHNOLOGY
Highest reliability & enhanced crack tolerance MBB module
PID
ENDURING HIGH PERFORMANCE
Anti LID and Anti PID Technology. Under long-term production safety conditions, the limited power degradation caused by the PID effect is guaranteed.
EXTREME WEATHER RATING
High-tech aluminum alloy frame, certified for high snow (5400 Pa) and wind loads (2400 Pa).
ALL-WEATHER TECHNOLOGY Optimal
Yields, whatever the weather, with low-light and temperature behaviour.
Residential
Utility
Off-Grid
Commercial
THE IDEAL SOLUTION FOR
COMPREHENSIVE CERTIFICATES
IEC 61215 | IEC 61730 | IEC 61701 | IEC 62716
LINEAR PERFORMANCE WARRANTY
12-year Warranty for Materials and Processing (1st year ≤ 1.0%, 2nd~30th years ≤ 0.40% / year)
30-year Warranty for Extra Linear Power Output
Product warranty
12
Years
Product warranty
30
Years
80%
85%
100%
99%
95%
1
5
10
15
25
30
90%
ADDED VALUE FROM WARRANTY
years
87.40%
20
Guaranteed Power Performance
MADE IN UAE
Premium products are 100% made in the Emirates.
A RELIABLE INVESTMENT
Products up to 725Wp, 30 years of performance warranty.
ENCOURAGING INNOVATION
Innovative, prestigious, European production technology
ADVANTAGES
MAXIMUM EFFICIENCY
23.3%
OUTPUT POSITIVE TOLERANCE
Guaranteed 0~+10W positive tolerance ensures power output reliability.
MAXIMUM POWER OUTPUT
+10W
725W
Address: Abundance Solar Panels Industries – LLC Plot No 7-8, KHIA5, KEZAD, Abu Dhabi, UAE
UL 61730 | CEC | ISO 9001 | ISO 14001| ISO 45001

## Slide 2
ENGINEERING DRAWINGS & TECHNICAL PARAMETERS
ABS-132GWS-G12-705-725W
ELECTRICAL CHARACTERISTICS (STC/NOCT)
Models | Maximum Rating Power (Pmax) (W) |  | Open Circuit Voltage (Voc) (V) |  | Maximum Power Voltage (Vmp) (V) |  | Short Circuit Current (Isc) (A) |  | Maximum Power Current (Imp) (A) |  | Module Eﬃciency (EFF)(%)
 | STC | NOCT | STC | NOCT | STC | NOCT | STC | NOCT | STC | NOCT | 
ABS-132GWS-G12-705 | 705 | 527.0 | 47.06 | 44.25 | 40.57 | 37.85 | 18.10 | 14.61 | 17.43 | 13.96 | 22.70%
ABS-132GWS-G12-710 | 710 | 530.7 | 47.17 | 44.35 | 40.66 | 37.94 | 18.14 | 14.64 | 17.54 | 14.05 | 22.86%
ABS-132GWS-G12-715 | 715 | 534.4 | 47.22 | 44.40 | 40.71 | 37.98 | 18.17 | 14.66 | 17.59 | 14.09 | 23.02%
ABS-132GWS-G12-720 | 720 | 538.2 | 47.34 | 44.51 | 40.81 | 38.08 | 18.21 | 14.69 | 17.69 | 14.17 | 23.18%
ABS-132GWS-G12-725 | 725 | 541.9 | 47.44 | 44.60 | 40.90 | 38.16 | 18.23 | 14.71 | 17.79 | 14.25 | 23.34%
*Standard Test Condition (STC): Cell Temperature 25 °C, Irradiance 1000 W/m², AM 1.5, Nominal module operating temperature (NMOT): Air mass AM 1.5, Irradiance 800W/m², temperature 20°C, windspeed 1 m/s. Reduction in eﬃciency from 1000W/m² to 200W/m² at 25°C: 3.5 ± 2%. *Values without tolerance are typical numbers. Measurement tolerance: ± 3%```
Solar Cell | Topcon 210 x 105 mm G12 ,18BB
No.of cells | 132 (6×22)
Dimensions | 2384 mm x 1303 mm x 30 mm ( 93.85” x 51.30“ x 1.18” inch)
Weight | 35 kg / 77.16 lbs.(±3%)
Front Glass | 3.20 mm, High Transmission, Low Iron, Tempered ARC Glass
Cell Encapsulation | EPE(Expanded polyethylene) & EVA (Ethylene-Vinyl-Acetate)
Back Sheet | White Back Sheet
Frame | Silver Anodized Aluminum Alloy Type 6005T6 , Silver Color
Junction Box | IP68, 1500VDC, 3 Bypass Diodes
Connectors Type | IP68 MC4 Compatible
Cable | 400mm or 1300 mm, 4mm2
Package Conﬁguration | 36 pcs Per Pallet, 648 pcs per 40’ FT container ( Two pallets=One stack )
CURRENT-VOLTAGE CURVE UNDER DIFFERENT IRRADIANCE
1303±1
2384±1
FRONT VIEW
30
33
A-A
Laminate
Silicon Sealant
Frame
30
Laminate
Frame
15
B-B
Silicon Sealant
The Graphs are for reference purpose only. Please consult Abundance technical team for further clarifications.
BACK VIEW
B
C
1261± 2
400±1
1200±1
1400±1
A A
B B
Mechanical Load | 5400 Pa
Maximum System Voltage | 1500VDC
Series Fuse Rating | 30 A
Operating Temperature | -40 to 85 °C
Safety application class | Class II
Fire Rating | Class C
Nominal Module Operating Temperature | 43°C ± 2°C
Temperature Coeﬃcient of Isc | +0.05 % / °C
Temperature Coeﬃcient of Voc | -0.25 % / °C
Temperature Coeﬃcient of Pmax | -0.30 % / °C
OPERATING CONDITION
TEMPERATURE CHARACTERISTICS
MECHANICAL DATA
IV-CURVES
DIMENSIONS OF PV MODULE (mm)
Address: Abundance Solar Panels Industries – LLC Plot No 7-8, KHIA5, KEZAD, Abu Dhabi, UAE
800 W/ m 2
600 W/ m 2
400 W/ m 2
200 W/ m 2
25℃ 1000 W/ m 2
00
6
9
12
15
18
10
20
30
40
50
Voltage(V)
Current(A)
CURRENT-VOLTAGE CURVE UNDER DIFFERENT WORKING TEMPERATURES
1000 W/m 2
6
9
12
15
18
10℃
25℃
40℃
55℃
70℃
0
0 10
20
30
40
50
Voltage(V)
Current(A)
C-Mounting Hole 4 No’s
B-Mounting Hole 8 No’s